EFD Localization

Student Manual

A guide to the dataset, the underlying problem, and the message schemas you will work with during the ADB Safegate hackathon.

Code the Sky — ADB Safegate Hackathon

# Table of Contents

Table of Contents	2

1. Setting the Scene	3

1.1  What is an airfield lighting circuit?	3

1.2  What is an Earth Fault?	3

1.3  What is EFD Localization, and Why Is It Hard?	3

2. How the Telemetry Reaches You	5

2.1  Powerline Communication (PLC)	5

2.2  Repeaters and Wave Depth	5

3. The Dataset	6

3.1  How the Data Was Collected	6

3.2  File Structure and Naming	6

Fault resistance lookup	6

3.3  Inside a CSV File	7

3.4  Volume per scenario	7

4. The Four Message Types	8

4.1  COMM — Communication Statistics	8

4.2  RATES — Raw Response Rates per Wave Depth	9

4.3  EXCOMM — Extended Communication Diagnostics	9

4.4  CORR — Correlator Statistics	10

5. How to Approach the Problem	12

5.1  What you are being asked to deliver	12

5.2  Suggested first steps	12

5.3  Things to watch out for	12

6. Background Reference	14

6.1  Glossary	14

6.2  Quick Cross-Reference	15

6.3  Final Word	15

# 1. Setting the Scene

## 1.1  What is an airfield lighting circuit?

Airports use thousands of inset and elevated lights along runways, taxiways, and aprons to guide aircraft. Unlike the lights in a building (where each lamp is wired in parallel to a constant voltage), airfield lights are wired in series along a single loop of cable that can run several kilometres long. A cabinet at one end called a Constant Current Regulator (CCR) sends a regulated AC current — typically 6.6 amps — around the loop, and every fixture in the loop sees the same current.

Each fixture has a transformer that taps into this current and powers an LED light. Because all fixtures share one current loop, the system has very different failure modes from a parallel circuit: a short to ground anywhere on the loop affects the entire circuit, and the further the fault is from the regulator, the trickier it can be to isolate.

Why series? Why not parallel? A long parallel circuit would suffer huge voltage drop along the run — the lights at the far end would be much dimmer than those near the supply. A series circuit guarantees identical brightness at every fixture because each one sees the same current. The trade-off is that diagnosing a failure becomes harder, which is exactly the problem this case study is about.

## 1.2  What is an Earth Fault?

An earth fault, also called a ground fault, occurs when one of the conductors in the lighting loop develops an unintended electrical path to ground. In a healthy circuit, the current flows only between the two conductors of the loop. When a fault occurs, some of that current leaks to ground through whatever path the fault has created — damaged insulation, water ingress at a connector, a corroded fitting, or a damaged cable section.

The fault is characterized by an impedance — its electrical resistance to ground. A dead short (0 Ω) is a hard fault that the system detects immediately. A high-impedance fault (tens of kilo-ohms) is far more subtle: it leaks only a small amount of current, but is still a degradation of the circuit's safety and a potential precursor to a worse failure.

## 1.3  What is EFD Localization, and Why Is It Hard?

ADB Safegate's Earth Fault Detection (EFD) system can already tell that an earth fault exists somewhere on a circuit. What it cannot do is tell you exactly where on the loop the fault has occurred. Today, locating the fault is still a manual process: a technician walks the circuit with handheld test equipment, or isolates sections one at a time until the fault is found. Both approaches take significant time, especially on long runways, and each minute the circuit is offline is a minute the runway can't be used at full capacity.

Localization is hard for a fundamental reason: the entire circuit shares the same current. So you cannot point to one fixture's electrical reading and say "this fixture is the problem" the way you could in a parallel circuit. The localization signal, if it exists at all in the data we have, must come from more subtle effects: differences in how each fixture communicates with the regulator, changes in the quality of the powerline communication signal at fixtures near the fault, or patterns in alarms across the circuit.

The hackathon question ADB Safegate already collects communication telemetry from every fixture. The question this case study asks is: does that telemetry secretly carry spatial information about where faults occur? And if so, how do we extract it?

# 2. How the Telemetry Reaches You

## 2.1  Powerline Communication (PLC)

There are no separate data wires in an airfield lighting circuit. The same two conductors that deliver power to each fixture are also used to send commands and receive status. This is called Powerline Communication, or PLC: a high-frequency carrier signal is superimposed on the AC power waveform, and modems at each end demodulate it to extract the messages.

The CCR cabinet contains a master controller. Each fixture contains a remote (sometimes called a remote node or simply a "remote"). The master polls each remote in turn, asks for its status, and the remote answers by modulating the same powerline.

Why does PLC matter for fault localization? An earth fault doesn't only leak power current to ground — it leaks communication signal too. The PLC carrier is a real radio signal travelling along the cable, and any path to ground is, electrically speaking, a partial short of that signal. Fixtures near or beyond the fault may see a weaker, noisier, or more delay-prone communication channel than fixtures upstream of the fault. The pattern of communication degradation across the circuit is, in principle, a function of where the fault is. That is the proxy you will be working with.

## 2.2  Repeaters and Wave Depth

Sometimes the master cannot reach a remote on the first try — the signal at that fixture might be too weak, or the line might be noisy. The PLC system handles this by allowing fixtures to act as repeaters: a closer fixture relays the message to a more distant one. A "wave depth" of 0 means the master communicates directly with the fixture; a depth of 1 means one fixture in between is acting as a repeater; and so on, up to depth 7.

When the channel is healthy, most communication happens at depth 0. When the channel is degraded, more retries land at higher depths. The schemas you will see in the next section include both raw response rates per wave depth and aggregate statistics — both can carry signal about local channel health.

# 3. The Dataset

## 3.1  How the Data Was Collected

The dataset is from a controlled lab test conducted by ADB Safegate. The setup is summarised in the diagram below.

A CCR cabinet (specifically CCR6 in CSF mode at Power Step 1, on Comm Channel 7) feeds a series circuit of 90 Axon EQ v4 inset fixtures. Between the CCR and the first fixture there is roughly 1 km of field wire on each conductor — i.e., 2 km of wiring added before the fixture loop even begins. No additional wire was added between fixtures themselves. The fixtures were installed in their bottom pans during the test, with no top covers or light engines connected.

Earth faults were then deliberately introduced at four different physical locations along the circuit, at multiple resistance values per location, and the resulting PLC telemetry was recorded for roughly 15 minutes per scenario. The recording was repeated across three independent test runs (T0001, T0002, T0003) on three separate days using the same physical setup.

## 3.2  File Structure and Naming

The dataset is delivered as a ZIP containing three subfolders, one per test run:

EFD_T0001/, EFD_T0002/, EFD_T0003/

Each folder contains around 24-33 CSV files. Filenames follow a deliberate convention that encodes the test scenario:

<epoch>-<commCh>-<powerStep>-<faultLocation>-<faultResistance>.csv

Where:

- epoch — Unix timestamp of when the recording started, used as a unique file identifier

- commCh — Communication channel (always 7 in this dataset)

- powerStep — CCR power step (always 1 in this dataset)

- faultLocation — A code 0–4 representing one of four physical fault locations on the loop. Code 0 means no fault (baseline). Codes 1–4 are distinct physical points that ADB Safegate is keeping confidential — your algorithm needs to localize them, not look them up.

- faultResistance — A code 0–8 mapping to a fault resistance value via the lookup table below.

### Fault resistance lookup

The fault resistance code in the filename maps to an actual ohmic value as follows. This corresponds to Modbus register 40003 in the test rig setup.

| Code | Resistance | Description |
| --- | --- | --- |
| 0 | 0 Ω | Hard short (dead earth fault) |
| 1 | 5 kΩ | Low impedance fault |
| 2 | 14.3 kΩ | Moderate impedance fault |
| 3 | 19.3 kΩ | Moderate impedance fault |
| 4 | 30 kΩ | Higher impedance fault |
| 5 | 35 kΩ | Higher impedance fault |
| 8 | 50 kΩ | Very high impedance fault |

Note on missing codes Codes 6 and 7 do not appear in this dataset (they correspond to additional resistance combinations available on the test rig but not used during these particular runs). You will see codes 0, 1, 2, 3, 4, 5, and 8 in the filenames.

## 3.3  Inside a CSV File

Each CSV records around 15 minutes of telemetry from all 90 fixtures. The file has no header row — every line starts directly with data. Each line represents a single message, and there are four message types interleaved within the same file. The first two columns of every line tell you which type:

- Column 1: Unix timestamp of when the message arrived (seconds, with fractional precision)

- Column 2: Message type — one of four strings: COMM, RATES, EXCOMM, or CORR

- Column 3: Remote ID — the airfield ID of the fixture (1001 to 1090 in this dataset)

- Columns 4 onward: Payload fields specific to that message type — the next section explains each

The number of columns per row varies by message type COMM rows have 12 columns. RATES rows have 19 columns. EXCOMM rows have 8 columns. CORR rows have 9 columns. If you read the file directly with a single CSV header, you will get inconsistent results — you need to split rows by message type before parsing.

## 3.4  Volume per scenario

Within one CSV — i.e., one fault scenario, ~15 minutes of telemetry — every fixture appears multiple times in each message stream. Each fixture (Remote ID 1001–1090) typically reports about 92 COMM and 92 RATES messages, and about 20 EXCOMM and 20 CORR messages. The COMM/RATES messages are higher cadence; EXCOMM/CORR are diagnostic snapshots.

# 4. The Four Message Types

Every row in a CSV file is one of four message types. Each carries different information about the health and behaviour of the communication channel between the CCR and a single fixture. Below is the full schema for each, including what the fields mean physically and why they may matter for fault localization.

## 4.1  COMM — Communication Statistics

Aggregate communication statistics for one fixture. This is the workhorse message: it tells you whether the master is successfully reaching the remote, how many tries it took, and whether any repeaters were involved. (Internal Modbus reference: ASYNC_COMM_STATS, Table 3-137.)

| Column | Field | Type | Meaning |
| --- | --- | --- | --- |
| 1 | timestamp | float | Unix timestamp |
| 2 | (message type) | string | Always "COMM" |
| 3 | Remote Airfield ID | uint32 | Fixture ID (1001–1090) |
| 4 | Response Rate | uint32 | % of communication attempts that got a response (0–100) |
| 5 | Number of Attempts | uint32 | How many comm attempts were made |
| 6 | Number of Failures | uint32 | How many failed (no response or wrong response) |
| 7 | Downstream Avg Repeater Depth | float | Average wave depth, master → remote direction |
| 8 | Upstream Avg Repeater Depth | float | Average wave depth, remote → master direction |
| 9 | Downstream Current Repeater Depth | uint32 | Most recent wave depth, master → remote |
| 10 | Upstream Current Repeater Depth | uint32 | Most recent wave depth, remote → master |
| 11 | Average Receive Signal Strength | float | Average received signal level |
| 12 | Incorrect Count | uint32 | How many times the remote was found in the wrong state |

Sample row 1.75e+09, COMM, 1001, 100, 11, 0, 0.0, 0.0, 0, 0, 0.0, 0 → fixture 1001, 100% response rate, 11 attempts, 0 failures, all at depth 0, healthy.

Why it matters for localization Fixtures past or near a fault may show a degraded response rate, increased number of failures, or a non-zero average repeater depth — because the comm channel between them and the master is now noisier. The spatial pattern of these degradations across all 90 fixtures is what your algorithm should look for.

## 4.2  RATES — Raw Response Rates per Wave Depth

A more detailed breakdown of the response rate at each individual wave depth, in both directions. Where COMM gives you averages, RATES tells you the shape of the distribution: at which depth does this fixture actually communicate? (Internal Modbus reference: ASYNC_RAW_RATES, Table 3-139.)

| Column | Field | Type | Meaning |
| --- | --- | --- | --- |
| 1 | timestamp | float | Unix timestamp |
| 2 | (message type) | string | Always "RATES" |
| 3 | Remote Airfield ID | uint32 | Fixture ID |
| 4–11 | dsRawRate0 … dsRawRate7 | float (×8) | Downstream response rate at wave depth 0 through 7 (master → remote) |
| 12–19 | usRawRate0 … usRawRate7 | float (×8) | Upstream response rate at wave depth 0 through 7 (remote → master) |

Why it matters for localization RATES is the most spatially-rich message in this dataset. A fixture that drops from "100% at depth 0" to "60% at depth 0, 30% at depth 1, 10% at depth 2" tells you something specific is wrong with its direct path to the master. If many fixtures past a certain point on the loop show similar patterns, you have a localization signal.

## 4.3  EXCOMM — Extended Communication Diagnostics

Lower-level physical-layer diagnostics from the receiver. EXCOMM messages are less frequent than COMM/RATES (about once every 45 seconds per fixture) but they expose deeper hardware-level signal characteristics. (Internal Modbus reference: ASYNC_EX_COMM_STATS, Table 3-131.)

| Column | Field | Type | Meaning |
| --- | --- | --- | --- |
| 1 | timestamp | float | Unix timestamp |
| 2 | (message type) | string | Always "EXCOMM" |
| 3 | Remote ID | uint32 | Fixture ID |
| 4 | peakInputLevel | uint32 | Peak received signal level during the window (16-bit) |
| 5 | overflowStatus | uint32 | Bitmask of internal overflow conditions (8-bit). 0 = healthy. |
| 6 | berCount | uint32 | Bit Error Rate counter — number of bit errors detected (16-bit) |
| 7 | phaseNoise_dB | float | Phase noise of the received carrier, in dB. Less negative = noisier. |
| 8 | rxCrcFailCount | uint32 | Number of received messages that failed CRC checking (12-bit) |

Why it matters for localization Earth faults distort the carrier signal in physical ways: weakened amplitude (peakInputLevel), phase distortion (phaseNoise_dB), and increased corruption (berCount, rxCrcFailCount). EXCOMM may carry the strongest physical-layer fingerprint of the fault's spatial location, even when the higher-level COMM stats still show successful communication.

## 4.4  CORR — Correlator Statistics

Diagnostic statistics from the correlator stage of the receiver. The correlator is the part of the modem that detects whether an incoming signal matches the expected PLC waveform. It can fire on actual messages (correlated peaks) or on noise that happens to look message-shaped (uncorrelated peaks). (Internal Modbus reference: ASYNC_EX_CORR_STATS, Table 3-132.)

| Column | Field | Type | Meaning |
| --- | --- | --- | --- |
| 1 | timestamp | float | Unix timestamp |
| 2 | (message type) | string | Always "CORR" |
| 3 | Remote ID | uint32 | Fixture ID |
| 4 | peakCorrLevel_dB | float | Peak correlated signal level in dB — strength of true signal detection |
| 5 | peakUncorrLevel_dB | float | Peak uncorrelated signal level in dB — strength of noise detected |
| 6 | ftryCorrTrigCount | uint32 | How many times the factory correlator was triggered |
| 7 | userCorrTrigCount | uint32 | How many times the user correlator was triggered |
| 8 | corrFired | uint32 | Flag: did the user correlator fire? |
| 9 | ftryCorrFired | uint32 | Flag: did the discovery (factory) correlator fire? |

Why it matters for localization The ratio of correlated to uncorrelated peak levels is essentially a signal-to-noise indicator at the modem level. A circuit segment past an earth fault may see uncorrelated levels rise (more noise) while correlated levels drop (weaker true signal). A fixture-level pattern of degraded SNR can be a powerful localization cue.

# 5. How to Approach the Problem

## 5.1  What you are being asked to deliver

The full scope of the case study lives in the EFD_Localization_README.md in the repository. In short:

- A localization output. Given one CSV (one fault scenario), produce a ranked list of probable fault locations or zones.

- Honest confidence scoring. Don't just give a single guess — quantify how certain your method is, and acknowledge the cases where the data simply doesn't constrain the answer.

- Defensible logic. Justify your approach from engineering reasoning about how PLC signals propagate through a series airfield circuit, not just statistical correlation.

- A gap analysis. Tell us what existing telemetry was useful, what was unreliable, and what additional data (CCR readings, impedance measurements, fixture position metadata) would lift localization toward production-grade.

## 5.2  Suggested first steps

- Read the file format first. The schema differences between COMM, RATES, EXCOMM, and CORR rows are the most common source of bugs. Build a loader that splits one CSV into four DataFrames (one per message type) before doing anything else.

- Start with the baseline. The ...0-0.csv files are no-fault recordings. Compare the distributions of every metric across all 90 fixtures in a baseline file. This tells you what "normal" looks like for each fixture and metric — the noise floor against which fault scenarios should stand out.

- Pick a single faulted scenario. Look at a hard short (resistance code 0) at one location. The signal should be loudest here. If you can't see a localization pattern in this file, you won't see it in subtler ones.

- Visualise per-fixture metrics across all 90 IDs. For one or two metrics — Response Rate, peakInputLevel, phaseNoise_dB — make a plot of the metric versus the fixture ID. A spatial signal will show up as a discontinuity, a slope, or a clustered pattern across the 90 fixtures.

- Test generalization across the three runs. If your method works on T0001, does it still work on T0002 and T0003 with no parameter changes? Generalization across independent runs is a strong sanity check.

## 5.3  Things to watch out for

The filename leaks the answer The fault location and resistance are encoded directly in the filename (the last two segments). Do not use these as features. Treating the filename as ground truth defeats the purpose of the exercise. Read the filename only when validating your method's predictions against the truth, never inside your localization model itself.

Don't collapse the spatial signal It is tempting to compute one aggregate metric per fixture and stop there. But a fault at location 2 vs. location 4 will produce subtly different spatial patterns across the 90 fixtures. If you reduce to a single number, you throw away exactly the information that differentiates one location from another. Keep your features per-fixture wherever possible.

Honesty beats accuracy If your method is confident on hard shorts (resistance 0) but unable to localize 50 kΩ faults, say so. A localization tool that knows when it doesn't know is genuinely useful in production. A tool that always answers, even when wrong, is not.

# 6. Background Reference

## 6.1  Glossary

| Term | Meaning |
| --- | --- |
| Airfield Ground Lighting (AGL) | The category of lighting equipment used on runways, taxiways, and aprons to guide aircraft. |
| Axon EQ | ADB Safegate's brand of LED airfield lighting fixture, with onboard electronics and a PLC modem. |
| BER (Bit Error Rate) | The fraction of bits in a transmitted message that are received incorrectly. |
| Carrier | A high-frequency signal on which information is modulated for transmission — for PLC, the carrier rides on top of the AC power waveform. |
| CCR (Constant Current Regulator) | A power supply that delivers a constant AC current — typically 6.6 A — into a series airfield lighting loop. |
| Correlator | A receiver component that detects when an incoming signal matches a known pattern. Used to discriminate real messages from noise. |
| CRC (Cyclic Redundancy Check) | An error-detection code attached to a message to detect transmission errors. A CRC failure means the message arrived but was corrupted. |
| Earth fault / Ground fault | An unintended electrical path between a circuit conductor and ground. |
| EFD (Earth Fault Detection) | ADB Safegate's system for detecting that an earth fault is present somewhere on a circuit. |
| Fixture | An individual airfield light unit, typically containing an LED engine and a transformer. |
| Impedance | The total opposition a circuit presents to AC current flow, measured in ohms — combines resistance with reactance. |
| Master | The PLC controller in the CCR cabinet that polls remotes for status. |
| PLC (Powerline Communication) | A communication technology that sends data signals over the same conductors used for electrical power. |
| Phase noise | Random fluctuations in the phase of an oscillator's output, indicating imperfect frequency stability or interference. |
| Remote / Remote Node | The PLC interface inside each fixture that responds to the master's polls. |
| Repeater | A fixture that relays a message between the master and a more distant fixture when direct communication fails. |
| Series circuit | An electrical circuit in which all components carry the same current because they are wired in a single loop. |
| SNR (Signal-to-Noise Ratio) | The strength of a signal relative to background noise, in decibels. |
| Telemetry | Automated recording and transmission of measurements from a remote system to a central one. |
| Wave depth | In PLC, the number of repeater hops a message takes between master and remote (0 = direct, 7 = up to seven hops). |

## 6.2  Quick Cross-Reference

If you encounter one of these column or message names elsewhere, this table lets you jump back to the right schema:

| Where you see it | What it is | Refer to |
| --- | --- | --- |
| COMM in column 2 | ASYNC_COMM_STATS | Section 4.1 |
| RATES in column 2 | ASYNC_RAW_RATES | Section 4.2 |
| EXCOMM in column 2 | ASYNC_EX_COMM_STATS | Section 4.3 |
| CORR in column 2 | ASYNC_EX_CORR_STATS | Section 4.4 |
| dsRawRate0..7 | Downstream wave depth response rates | Section 4.2 |
| usRawRate0..7 | Upstream wave depth response rates | Section 4.2 |
| peakInputLevel | Physical-layer received signal level | Section 4.3 |
| phaseNoise_dB | Carrier phase noise | Section 4.3 |
| berCount | Bit Error Rate counter | Section 4.3 |
| rxCrcFailCount | Receive CRC failure count | Section 4.3 |
| peakCorrLevel_dB | Correlator peak signal | Section 4.4 |
| peakUncorrLevel_dB | Correlator peak noise | Section 4.4 |
| Wave depth | Number of repeater hops | Section 2.2 |
| Modbus register 40003 | Maps fault resistance code to ohmic value | Section 3.2 |